NOTLA WATER AUTHORITY

Calendar Year 2025

WATER QUALITY REPORT

P.O. Box 609							Water System ID: 2910003

Blairsville, GA 30514

Notla Water Authority is pleased to report that our community’s drinking water met or exceeded all safety and quality standards set by the State of Georgia and EPA during the previous year.  This 2025 Water Quality Report provides our customers with detailed accounts of all the monitoring and testing results gathered from water quality testing from January through December 2024. Our employees are committed to working tirelessly to advance the effectiveness of the water system and to provide clean, safe and reliable water.  Currently, NWA customers receive blended water from the surface treatment plant and groundwater wells located throughout the water system.

The Safe Drinking Water Act (SDWA) requires that all Community Water Systems provide an annual Water Quality Report to their customers.  This report contains information that will enable the consumer to make educated health related decisions concerning the consumption of their drinking water by including details of where their water comes from, what it contains, and the risks the water testing and treatment are designed to prevent.

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that the water poses a health risk.  More information about contaminants and potential health effects can be obtained by calling the EPA’s Safe Drinking Water Hotline (1-800-426-4791).

Some people may be more vulnerable to contaminants in drinking water than the general population.  Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections.  These people should seek advice about drinking water from their health care providers.  EPA/CDC guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and other microbial contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).

The sources of drinking water (both tap and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells.  As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.

For more information about the system or this report, please contact Jennifer Maier at (706) 745-4598.  The board meetings are scheduled for the third Tuesday of each month at the NWA’s office.  Please call our office for the time.

Contaminants that may be present in source water include the following:

- Microbial contaminants, such as viruses and bacteria that may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.

- Inorganic contaminants, such as salts and metals, which can be naturally occurring or result from urban storm runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.

- Pesticides and herbicides, which may come from a variety of sources such as agriculture, urban storm water runoff, and residential uses.

- Organic chemical contaminants, including synthetic and volatile organic chemicals, which are by-products of industrial processes and petroleum production, and can also come from gas stations, urban storm water runoff, and septic systems.

- Radioactive contaminants, which can be naturally occurring or be the result of oil and gas production and mining activities.

In order to ensure that tap water is safe to drink, EPA prescribes regulations that limit the amounts of certain contaminants in water provided by public water systems.  Food and Drug Administration regulations establish limits for contaminants in bottled water which must provide the same protection for health.

SPANISH: Este informe contiene información muy importante sobre su agua potable. Tradúzcalo o hable con alguien que lo entienda bien.

WATER QUALITY DATA

The attached table lists the drinking water contaminants that were detected during 2025.  The presence of contaminants in the water does not necessarily indicate that the water poses a health risk.  The data contained in the table is from testing conducted from January 1st through December 31 of 2025, unless otherwise noted.  EPD requires us to monitor for certain contaminants less than once per year because the concentration of these contaminants is not expected to vary significantly from year to year.  Some of the data, though representative of the water quality, is more than a year old.

Terms and Abbreviations:

Maximum Contaminant Level (MCL): “The highest level of a contaminant that is allowed in drinking water.  MCLs are set as close to the MCLGs as feasible using the best available treatment technology.”

Maximum Contaminant Level Goal (MCLG): “The level of a contaminant in drinking water below which there is no known or expected risk to health.  MCLGs allow for a margin of safety.”

Treatment Technique (TT): “A required process intended to reduce the level of a contaminant in drinking water.”

Turbidity: “A measure of the cloudiness of water.”

Action Level (AC): “The concentration of a contaminant which, if exceeded, triggers treatment or other requirements which a water system must follow.”

Maximum Residual Disinfectant Level (MRDL): “The highest level of a disinfectant allowed in drinking water.  There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.”

Maximum Residual Disinfectant Level Goal (MRDLG): “The level of a drinking water disinfectant below which there is no known or expected risk to health.  MRDLGs do not reflect the benefits of the use of disinfectants to control microbiological contaminants.”

Reporting Limit (RL):  Level at which a contaminant is reported on the Consumer Confidence Report.

Variances and Exemptions: “State or EPA permission not to meet an MCL or a treatment technique under certain conditions.”

More Abbreviations:

n/a:  not applicable

nd:  not detectable at testing limits

ns:  no standard

mg/L:  milligrams per liter

μg/L:  micrograms per liter

ppb:  parts per billion or micrograms per liter

ppm:  parts per million or milligrams per liter

pCi/l:  picocuries per liter (a measure of radiation)

NTU:  instrumental measurement of water clarity

< :  less than

| 2025 DETECTED CONTAMINANTS TABLE |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ORGANIC COMPOUNDS (OC) |  |  |  |  |  |  |  |  |  |  |
|  |  | MCL/AL |  | Detected |  | Sample |  |  |  |  |
| Contaminant |  | MRDL | Units | (Avg) | Range | Year |  | Violations | Typical Source of Contamination |  |
| Total Organic Carbon |  | n/a | ppm | 0.92 | 0.81-1.02 | 2025 |  | No | Natural organics in water |  |
| INORGANIC COMPOUNDS (IOC) |  |  |  |  |  |  |  |  |  |  |
|  |  | MCL/ |  | Detected |  | Sample |  |  |  |  |
| Contaminant |  | AL | Units | (Max) | Range | Year |  | Violations | Typical Source of Contamination |  |
| Lead (ppb) |  | AL: 15 | ppb |  | 0-26 | 2023 |  | No | Corrosion of household plumbing |  |
|  |  | *Two samples were found to have lead levels in excess of the Action Level of 15 ppb. |  |  |  |  |  |  |  |  |
| 90th Percentile: Lead |  | AL: 15 | ppb | 1 |  | 2023 |  | No | Corrosion of household plumbing |  |
| Copper (ppm) |  | AL: 1.3 | ppm |  | 0-0.320 | 2023 |  | No | Corrosion of household plumbing |  |
|  |  | No samples were found to have copper levels in excess of the Action Level of 1.3 ppm. |  |  |  |  |  |  |  |  |
| 90th Percentile: Copper |  | AL: 1.3 | ppm | 0.04 |  | 2023 |  | No | Corrosion of household plumbing |  |
| Fluoride |  | 4.0 | ppm | 0.7 | 0.1-1.1 | 2025 |  | No | Water additive which promotes strong teeth |  |
| Nitrates/Nitrites |  | 10.0 | ppm | 1.09 | 0-1.09 | 2025 |  | No | Runoff from fertilizer use; leaching from septic |  |
|  |  |  |  |  |  |  |  |  | tanks; sewage; erosion of natural deposits |  |
| Sodium |  | n/a | ppb | 7200 |  | 2025 |  | No | Erosion of natural deposits; runoff |  |
| VOLATILE ORGANIC COMPOUNDS (VOC) |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Detected |  | Sample |  |  |  |  |
| Contaminant |  | MCL | Units | (Max) | Range | Year |  | Violations | Typical Source of Contamination |  |
| Bromodichloromethane |  | 80 | ppb | 3.18 | 0-3.18 | 2025 |  | No | By-product of drinking water chlorination |  |
| Chloroform |  | 80 | ppb | 34.0 | 0-34.0 | 2025 |  | No | By-product of drinking water chlorination |  |
| DISINFECTANTS & DISINFECTION BY-PRODUCTS |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Detected |  | Sample |  |  |  |  |
| Contaminant |  | MCL | Units | (Max) | Range | Year |  | Violations | Typical Source of Contamination |  |
| Chlorine Residual |  | 4.0 | ppm | 2.3 | 0.5-2.3 | 2025 |  | No | Water Disinfectant |  |
| TTHMs Site #501 LRAA |  | 80 | ppb | 20.18 | 18.45-20.18 | 2025 |  | No | By-product of drinking water chlorination |  |
| TTHMs Site #502 LRAA |  | 80 | ppb | 25.00 | 16.08-25.00 | 2025 |  | No | By-product of drinking water chlorination |  |
| HAA5 Site #501 LRAA |  | 60 | ppb | 27.88 | 27.03-27.88 | 2025 |  | No | By-product of drinking water chlorination |  |
| HAA5 Site #502 LRAA |  | 60 | ppb | 19.59 | 5.03-19.59 | 2025 |  | No | By-product of drinking water chlorination |  |
| RADIOACTIVE CONTAMINANTS |  |  |  |  |  |  |  |  |  |  |
|  |  | MCL/ |  | Detected |  | Sample |  |  |  |  |
| Contaminant |  | [SMCL] | Units | (Max) | Range | Date |  | Violations | Typical Source of Contamination |  |
| Gross Alpha |  | 16 | pCi/l | < 3 |  | 2025 |  | No | Erosion of natural deposits |  |
| Ra-226 + Ra-228 |  | 5 | pCi/l | < 1 |  | 2025 |  | No | Erosion of natural deposits |  |
| Lead & Copper: Lead and copper may be found in household plumbing fixtures such as service lines, pipes, |  |  |  |  |  |  |  |  |  |  |
| solders and fluxes, and brass and bronze fixtures. Lead is found throughout the environment in the air, soil, |  |  |  |  |  |  |  |  |  |  |
| water, and household dust, and in consumer products, such as food, lead-based paint, pottery, porcelain and |  |  |  |  |  |  |  |  |  |  |
| pewter. Lead and copper enter drinking water primarily as a result of the corrosion, or wearing a way of |  |  |  |  |  |  |  |  |  |  |
| materials containing these metals. |  |  |  |  |  |  |  |  |  |  |
| Lead in drinking water is primarily from materials and parts used in service lines and in-home plumbing. |  |  |  |  |  |  |  |  |  |  |
| Notla Water is responsible for providing high quality drinking water and removing lead pipes but cannot |  |  |  |  |  |  |  |  |  |  |
| control the variety of materials used in the plumbing in your home. Because lead levels may vary over time, |  |  |  |  |  |  |  |  |  |  |
| lead exposure is possible even when your tap sampling results do not detect lead at one point in time. You |  |  |  |  |  |  |  |  |  |  |
| can help protect yourself and your family by identifying and removing lead materials within your home plumbing |  |  |  |  |  |  |  |  |  |  |
| and taking steps to reduce your family's risk. Using a filter certified by an American National Standards |  |  |  |  |  |  |  |  |  |  |
| Institute accredited certifier to reduce lead, is effective in reducing lead exposures. Follow the instructions |  |  |  |  |  |  |  |  |  |  |
| provided with the filter to ensure the filter is used properly. Use only cold water for drinking, cooking, or |  |  |  |  |  |  |  |  |  |  |
| making baby formula, flush your pipes for several minutes. You can do this by running your tap, taking a |  |  |  |  |  |  |  |  |  |  |
| shower, doing laundry or a load of dishes. If you have a lead service line or galvanized requiring replacement |  |  |  |  |  |  |  |  |  |  |
| service line, you may need to flush your pipes for a longer period. If you are concerned about lead in your |  |  |  |  |  |  |  |  |  |  |
| water and wish to have your water tested, contact Notla Water. Information on lead in drinking water, |  |  |  |  |  |  |  |  |  |  |
| testing methods, and steps you can take to minimize exposure is available at https://www.epa.gov/safewater/lead. |  |  |  |  |  |  |  |  |  |  |
| To access the Service Line Inventory (SLI) for Notla Water (GA2910003), visit the GA EPD Public Transparency Dashboard at https://ga-epd.120water-ptd.com. |  |  |  |  |  |  |  |  |  |  |
| The US EPA has established an "action level" of 15 ppb for lead and 1.3 ppm for copper. If concentrations |  |  |  |  |  |  |  |  |  |  |
| measured in your household water exceed these "action levels", you can minimize your exposure by: |  |  |  |  |  |  |  |  |  |  |
|  | * flushing the cold water faucet until the water becomes as cold as it will get |  |  |  |  |  |  |  |  |
|  | * using cold water for drinking or cooking. |  |  |  |  |  |  |  |  |
|  | * not cooking with or consuming water from the hot water faucet. |  |  |  |  |  |  |  |  |
|  | * not using hot water for making baby formula. |  |  |  |  |  |  |  |  |
| Nitrate: Nitrate in drinking water at levels above 10 ppm is a health risk for infants of less than 6 months of age. |  |  |  |  |  |  |  |  |  |  |
| High nitrate levels in drinking water can cause "blue baby syndrome." Nitrate levels may rise quickly for short |  |  |  |  |  |  |  |  |  |  |
| periods of time because of rainfall or agricultural activity. If you are caring for an infant you should ask advice |  |  |  |  |  |  |  |  |  |  |
| from your health care provider. |  |  |  |  |  |  |  |  |  |  |
| Waivers: Notla Water Authority has been issued a waiver certificate which exempts the system from monitoring |  |  |  |  |  |  |  |  |  |  |
| for thirty-two (32) regulated synthetic organic compounds (SOCs) and two (2) inorganic compounds (IOCs) listed in the GA Rule for Safe Drinking Water. Notla Water Authority was issued this waiver because the baseline monitoring demonstrates that the system’s drinking water complies with the chemical monitoring standards of the Georgia Rules for Safe Drinking Water for asbestos, cyanide and all synthetic organic compounds (SOC), including dioxin; and the system’s raw and treated water is not in a high potential pollution risk situation as determined by the following assessment plans: Vulnerability Assessment, Well Head Protection Plan, and Source Water Assessment. TOC: The percentage of Total Organic Carbon (TOC) removal was measured each month and the system met all TOC removal requirements set by the Georgia Rules for Safe Drinking Water. |  |  |  |  |  |  |  |  |  |  |